## Sheet1
CUP | CUP User Category | CUP User Inputs | CUP User Values
CUP | Setpoints | Hot Water Supply
CUP | Setpoints | Hot Water Supply Losses | -5
CUP | Setpoints | Hot Water Return Losses | -3
CUP | Setpoints | Chilled Water Supply
CUP | Setpoints | Chilled Water Supply Losses | 2
CUP | Setpoints | Chilled Water Return Losses | 0
CUP | Heat Pumps | Heating Capacity | 35000000
CUP | Heat Pumps | Cooling Capacity | 28000000
CUP | Heat Pumps | Water-Source Only % | 100%
CUP | Heat Pumps | Air-Source + Water Source % | 0%
CUP | Electric Boilers | Max Capacity | 3000000
CUP | Electric Boilers | Boiler Efficiency | 99%
CUP | Electric Boilers | Hot Water Setpoint | 170
CUP | Electric Chillers | Max Capacity | 25000000
CUP | Electric Chillers | Max Lift | 42
CUP | Electric Chillers | Min Lift | 15
CUP | Electric Chillers | Capacity for Min Lift
CUP | Heat Source/Sink | Ground-source Capacity | 20000000
CUP | Heat Source/Sink | Ocean Capacity | 1000000
CUP | Heat Source/Sink | Cooling Tower Capacity | 1000000
CUP | Heat Source/Sink | Delta T (for HPs; CT & Ocean Only) | 10
CUP | Heat Source/Sink | Delta T (for Cent. Chillers; CT & Ocean Only) | 15
Note on C16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Just to be clear, this will be a lookup table or a formula. Depending on different boiler loads, the efficiency will be different. Placeholder for now is ok

## Sheet2
Building | Building Level Categories | Building Level User Inputs | Building Level Values
Building | Heating Hot Water | Max Load
Building | Heating Hot Water | Delta T @ Max Load | 30
Building | Heating Hot Water | Delta T @ Min Load | 25
delta T
Building | Return HHW Temps given Supply Temp | 110 | 15
Building | Return HHW Temps given Supply Temp | 130 | 20
Building | Return HHW Temps given Supply Temp | 160 | 30
Building | Return HHW Temps given Supply Temp | 180 | 40
Building | Chilled Water | Max Load
Building | Chilled Water | Delta T @ Max Load | 16
Building | Chilled Water | Delta T @ Min Load | 8
Building | Domestic Hot Water | Max Load
Building | Domestic Hot Water | Max Approach | 20
Building | Domestic Hot Water | Min Approach | 5
Building | Domestic Hot Water | Load @ Min Approach

## Sheet3
TES | TES Tank User Categories | TES Tank User Inputs | Value
TES | Initial Conditions | Starting TES Hot Charge | 95%
TES | Initial Conditions | TES Hot Tank Upper Tank Temp | 170
TES | Initial Conditions | TES Hot Tank Lower Tank Temp | 80
TES | Initial Conditions | TES Hot Tank Upper Tank Volume
TES | Initial Conditions | TES Hot Thermocline thickness | 2
TES | Initial Conditions | TES Hot Thermocline volume
TES | Initial Conditions | TES Hot Tank Lower Tank Volume
TES | Initial Conditions | Starting TES Cold Charge | 95%
TES | Initial Conditions | TES Cold Tank Upper Tank Temp | 60
TES | Initial Conditions | TES Cold Tank Lower Tank Temp | 44
TES | Initial Conditions | TES Cold Tank Upper Tank Volume
TES | Initial Conditions | TES Cold Thermocline thickness | 2
TES | Initial Conditions | TES Cold Thermocline volume
TES | Initial Conditions | TES Cold Tank Lower Tank Volume
TES | Tank Properties | TES Hot Wall-Losses | 3%
TES | Tank Properties | TES Hot Thermocline/other-Losses | 19%
TES | Tank Properties | TES Cold Wall-Losses | 2%
TES | Tank Properties | TES Cold Thermocline/other-Losses | 2%
TES | Tank Properties | TES Hot Diameter | 50
TES | Tank Properties | TES Hot Height | 20
TES | Tank Properties | TES Hot Tank Volume
TES | Tank Properties | TES Cold Diameter | 60
TES | Tank Properties | TES Cold Height | 60
TES | Tank Properties | TES Cold Tank Volume
TES | Tank Charging Characteristics | TES Hot Capacity
TES | Tank Charging Characteristics | TES Cold Capacity
TES | Tank Charging Characteristics | TES Hot Max % of Total Tank Volume moved in 1 hr | 8%
TES | Tank Charging Characteristics | TES Cold Max % of Total Tank Volume moved in 1 hr | 8%
TES | Tank Charging Characteristics | TES Hot Max Flow
TES | Tank Charging Characteristics | TES Cold Max Flow
TES | Tank Charging Characteristics | Fraction of Thermocline to discharge | 50%
TES | Tank Charging Characteristics | Stop Charging tank at ____ Capacity | 98%
TES | Conversion Rates | CUF to GAL | 7.48
TES | Conversion Rates | GAL to Lbs | 8.34
Note on C35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Separate charge/discharge fractions. Charge as fully as possible, discharge 0% of thermocline

## Sheet4
Schedules | Load Shift Control | Month | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Total
Schedules | Load Shift Control - Hot Tank by month | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Schedules | Load Shift Control - Hot Tank by month | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0

## Sheet5
Schedules | Load Shift Control | Month | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Total
Schedules | Load Shift Control - Cold Tank by month | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 9 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
Schedules | Load Shift Control - Cold Tank by month | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1

## Sheet6
Schedules | Hot Water Setpoint | Schedules Month | CUP | Building
Schedules | Hot Water Setpoint | 1 | 170 | 130
Schedules | Hot Water Setpoint | 2 | 170 | 130
Schedules | Hot Water Setpoint | 3 | 170 | 130
Schedules | Hot Water Setpoint | 4 | 170 | 130
Schedules | Hot Water Setpoint | 5 | 170 | 130
Schedules | Hot Water Setpoint | 6 | 170 | 130
Schedules | Hot Water Setpoint | 7 | 170 | 130
Schedules | Hot Water Setpoint | 8 | 170 | 130
Schedules | Hot Water Setpoint | 9 | 170 | 130
Schedules | Hot Water Setpoint | 10 | 170 | 130
Schedules | Hot Water Setpoint | 11 | 170 | 130
Schedules | Hot Water Setpoint | 12 | 170 | 130

## Sheet7
Schedules | Schedules Category | Month | Building
Schedules | Domestic Water Temperature | 1 | 55
Schedules | Domestic Water Temperature | 2 | 55
Schedules | Domestic Water Temperature | 3 | 55
Schedules | Domestic Water Temperature | 4 | 55
Schedules | Domestic Water Temperature | 5 | 60
Schedules | Domestic Water Temperature | 6 | 60
Schedules | Domestic Water Temperature | 7 | 60
Schedules | Domestic Water Temperature | 8 | 60
Schedules | Domestic Water Temperature | 9 | 60
Schedules | Domestic Water Temperature | 10 | 60
Schedules | Domestic Water Temperature | 11 | 55
Schedules | Domestic Water Temperature | 12 | 55

## Sheet8
Schedules | Schedules Category | Month | CUP
Schedules | Chilled Water Setpoint | 1 | 44
Schedules | Chilled Water Setpoint | 2 | 44
Schedules | Chilled Water Setpoint | 3 | 44
Schedules | Chilled Water Setpoint | 4 | 44
Schedules | Chilled Water Setpoint | 5 | 44
Schedules | Chilled Water Setpoint | 6 | 44
Schedules | Chilled Water Setpoint | 7 | 44
Schedules | Chilled Water Setpoint | 8 | 44
Schedules | Chilled Water Setpoint | 9 | 44
Schedules | Chilled Water Setpoint | 10 | 44
Schedules | Chilled Water Setpoint | 11 | 44
Schedules | Chilled Water Setpoint | 12 | 44
Schedules | Cooling Tower Approach | 1 | 8
Schedules | Cooling Tower Approach | 2 | 8
Schedules | Cooling Tower Approach | 3 | 9
Schedules | Cooling Tower Approach | 4 | 10
Schedules | Cooling Tower Approach | 5 | 10
Schedules | Cooling Tower Approach | 6 | 10
Schedules | Cooling Tower Approach | 7 | 10
Schedules | Cooling Tower Approach | 8 | 10
Schedules | Cooling Tower Approach | 9 | 10
Schedules | Cooling Tower Approach | 10 | 10
Schedules | Cooling Tower Approach | 11 | 9
Schedules | Cooling Tower Approach | 12 | 8
Schedules | Ocean Return Temps | 1 | 55
Schedules | Ocean Return Temps | 2 | 55
Schedules | Ocean Return Temps | 3 | 56
Schedules | Ocean Return Temps | 4 | 58
Schedules | Ocean Return Temps | 5 | 60
Schedules | Ocean Return Temps | 6 | 65
Schedules | Ocean Return Temps | 7 | 67
Schedules | Ocean Return Temps | 8 | 70
Schedules | Ocean Return Temps | 9 | 70
Schedules | Ocean Return Temps | 10 | 68
Schedules | Ocean Return Temps | 11 | 60
Schedules | Ocean Return Temps | 12 | 58

## Sheet9
Schedules | Ground Return Temps | Schedules Month | Ht Rej - LWT* | Ht Rej - EWT | Ht Ex - LWT* | Ht Ex - EWT
Schedules | Ground Return Temps | 1 | 70 |  | 60
Schedules | Ground Return Temps | 2 | 65 |  | 55
Schedules | Ground Return Temps | 3 | 60 |  | 50
Schedules | Ground Return Temps | 4 | 62 |  | 52
Schedules | Ground Return Temps | 5 | 65 |  | 55
Schedules | Ground Return Temps | 6 | 70 |  | 60
Schedules | Ground Return Temps | 7 | 75 |  | 65
Schedules | Ground Return Temps | 8 | 80 |  | 70
Schedules | Ground Return Temps | 9 | 84 |  | 74
Schedules | Ground Return Temps | 10 | 85 |  | 75
Schedules | Ground Return Temps | 11 | 80 |  | 70
Schedules | Ground Return Temps | 12 | 75 |  | 65